## Issues
Label | Issue | Suggestions | Preventive Action
0 | No issue detected - your device is working properly | No Suggestions | P0
1 | 1st stage hot sump failure issue | Rebuild 1st stage | P1
2 | 1st stage compressor start components issue | Verify 1st stage with an analyzer if any issues with compressor or start components | P2
3 | 1st stage compression failure | Rebuild 1st stage | P3
4 | 1st stage issue | Verify if any leak in the 1st stage with leak detector. Verify 1st stage with an analyzer if any issues with compressor or start components | P4
5 | 1st stage leak issue | Verify if any leak in the 1ststage with leak detector. | P5
6 | 1st stage low charge issue | Add refrigerant as per the data plate. | P6
7 | 2nd stage hot sump issue | Rebuild 2nd stage | P7
8 | 2nd stage compressor start components issue | Verify 2nd stage with an analyzer if any issues with compressor or start components | P8
9 | 2nd stage compression failure | Rebuild 2nd stage | P9
10 | 2nd stage issue | Verify if any leak in the 2nd stage with leak detector. Verify 2nd stage with an analyzer if any issues with compressor or start components | P10
11 | 2nd stage leak issue | Verify if any leak in the 2nd stage with leak detector. | P11
12 | 2nd stage insulation issue (Armaflex) | Check Armaflex insulation 2nd stage | P12
13 | 2nd stage low charge issue | Add refrigerant as per the data plate. | P13
14 | Intermittent Fan Issue | Verify the condenser coil, condenser filter and condenser for any dust or dirt accumulation and the fan motor operation, replace the fan motor if found defective. | P14
15 | VIP Panel Issues | N/A | P15
16 | HSLC | N/A | P16

## Verification
TCs | Actual Name | Increasing | Decreasing
TC1 | 1st stage suction | The temperature found is rising outside this range, it indicates an issue with the system, which may impact the efficiency of the refrigeration cycle. Specifically, if the temperature is increasing, the system may be struggling to maintain its cooling capacity. | The temperature found is falling outside this range, it indicates an issue with the system, which may impact the efficiency of the refrigeration cycle. The system is getting colder from its desired range.
TC2 | Air lnlet | The temperature at the air inlet is outside the expected range, this could mean the condenser isn't working effectively or there is an issue with air circulation.The system is struggling to maintain its cooling capacity. | N/A
TC7 | Liquid line | The temperature found increases, it could indicate a problem with the condenser or a potential refrigerant flow issue. The liquid line is slightly warmer than the air inlet temperature. | N/A
TC8 | 1st sump | Within normal operational limits, it should not significantly fluctuate . A rise in temperature might suggest insufficient cooling, likely due to poor heat transfer in the sump area. | Within normal operational limits, it should not significantly fluctuate . A drop in temperature might suggest sufficient cooling, likely there is not an issue with the sump area.
TC10 | BPHX | If BPHX rises above the expected temperature range, it suggests a potential issue in the first stage of the refrigeration system, such as improper defrost cycles or a compressor failure, leading to inefficiencies in heat exchange. | If BPHX falls below the expected temperature range, it indicates a possible malfunction in the second stage of the refrigeration system, which could be related to issues like reduced refrigerant flow or problems with the heat exchange process.
TC3 | Evaporator inlet | An increase in Evaporator Inlet could indicate a disruption in the refrigerant flow or an issue with heat exchange, as this temperature should generally remain stable with only slight variations. | A decrease in Evaporator Inlet may suggest a drop in refrigerant flow or a problem with the heat exchange process, as it typically maintains a stable temperature with minimal fluctuation.
TC4 | Evaporator outlet | An increase in Evaporator outlet could signal potential issues with the heat exchange efficiency or refrigerant distribution, as the temperature should remain relatively constant with only minor variations. | A decrease in Evaporator outlet may point to a problem with refrigerant flow or the heat exchange system, as the temperature should generally remain stable with slight fluctuations.
TC6 | 2nd stage suction | A rise in temperature outside of the normal range suggests a malfunction in the refrigeration cycle, potentially caused by blockages, leaks, or other operational issues. | A fall in temperature outside of the normal range may indicate a problem in the refrigeration cycle, such as blockages, leaks, or other operational failures.
TC9 | 2nd Sump | If the 2nd Sump rises above the normal range, it suggests insufficient cooling, possibly due to poor heat transfer in the sump area, leading to system inefficiencies. | If the 2nd Sump falls and exceeds -96°C, the system will generate an alarm indicating 'Compressor Temperature Exceeded.' This could be caused by insufficient cooling returning to the compressor or a potential refrigerant leak.
RTD | Control probe | A deviation here would indicate a potential failure in the control system, causing an imbalance in temperature regulation. | N/A

## Condition
Issue | TC Involved
1st stage hot sump failure issue | TC8
1st stage compressor start components issue
1st stage compression failure | RTD, TC10, TC1, TC3, TC4
1st stage issue | RTD, TC10, TC1
1st stage leak issue | RTD, TC10, TC1, TC8, TC3, TC4
1st stage low charge issue | RTD, TC1, TC10
2nd stage hot sump issue | TC9
2nd stage compressor start components issue | RTD, TC1, TC6, TC8, TC9, TC10
2nd stage compression failure | RTD, TC1, TC3, TC4, TC10
2nd stage issue | RTD, TC10, TC6, TC1
2nd stage leak issue | RTD, TC1, TC3, TC4, TC6, TC10
2nd stage insulation issue (Armaflex) | RTD, TC3, TC4, TC6, TC10, TC1, TC9
2nd stage low charge issue | RTD, TC3, TC10, TC6, TC4
Intermittent Fan Issue | RTD, TC2, TC7
VIP Panel Issues
HSLC | RTD, Stage 1 RPM,Stage 2 RPM